## Sheet1
Inputs:			Change to match size & materials
Heat generation inside	85	Watts	Average at steady state
Height	27	Inches	Enclosure Height
Width	22	Inches	Enclosure Width
Depth	22	Inches	Enclosure Depth
Wall R-value	6	in/(BTU*in/hr*ft*ft*F)	1 inch foam board
Top R-value	6	in/(BTU*in/hr*ft*ft*F)	1 inch foam board
Bottom R-value	0.74	in/(BTU*in/hr*ft*ft*F)	½ inch OSB (like Plywood)
Air Convention Coefficient	55	W/(m*m*C)	Do not change this

Intermediate Results:
Height	0.685801371602743	Meters
Width	0.558801117602235	Meters
Depth	0.558801117602235	Meters	Do not change calcs below
Wall Area	1.53290629161904	m*m
Top Area	0.312258689033507	m*m
Bottom Area	0.312258689033507	m*m
Wall RSI	1.05666172383794	m*m*C/W
Top RSI	1.05666172383794	m*m*C/W
Bottom RSI	0.130321612606679	m*m*C/W
Air Resistance 1 side	0.018181818181818	m*m*C/W
Wall Resistance	0.713041212093359	C/W
Top Resistance	3.50038413209467	C/W
Bottom Resistance	0.5338049983052	C/W
Total Resistance	0.280782960284708	C/W

Results:
Steady state Rise in box	23.8665516242002	C
	42.9597929235604	F